| PHYSICAL SPECIFICATION |
| --- |
| Nominal Voltage Nominal Capacity (10HR) | 12V 80Ah |  |
| Dimension | Length Width Container Height Total Height | 350±2mm （13.78 inches） 166±2mm (6.54 inches) 174±2mm (6.85 inches) 174±2mm (6.85 inches) |  |
| Weight | Approx. 23.1 Kg ( 50.91lbs) |  |
| Standard Terminal | Bolt-and-nut lead terminal Bolt Type: M6 |  |
| ELECTRICAL SPECIFICATION |
| Characteristics | Discharge curves @ 25℃ (77 °F) |
| Capacity | 10 hour rate (8A) 5 hour rate (13.6A) 3 hour rate (20A) 1hour rate (48A) | 80Ah 68Ah 60 48Ah |  |
| Capacity affected by temperature | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） | 102% 100% 85% |  |
| Internal Resistance | Full charged battery (25℃,77 0F) 7mΩ |  |
| Constant Voltage Charge | Cycle | Initial Charging Current less than 20A Voltage 14.1~14.4V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |
|  | Standby | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |