| PHYSICAL SPECIFICATION |
| --- |
| Nominal Voltage Nominal Capacity (10HR) | 2V 800Ah |  |
| Dimension | Length Width Container Height Total Height | 410±2mm （16.14 inches） 175±2mm (6.89 inches) 330±2mm (12.99inches) 365±2mm (14.37 inches) |  |
| Weight | Approx. 62Kg (136.24lbs) |  |
| Standard Terminal | Bolt-and-nuts terminal Bolt Type: M8 |  |
| ELECTRICAL SPECIFICATION |
| Characteristics | Discharge curves @ 25℃ (77 °F) |
| Capacity | 100 hour rate (8A) 50 hour rate (16A) 10 hour rate (40A) 1hour rate (520A) | 880Ah 840Ah 800Ah 520Ah |  |
| Capacity affected by temperature | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） | 102% 100% 85% |  |
| Designed life | ≥4200 Cycles @ 20% DOD (25℃) |  |
| Internal Resistance | Full charged battery (25℃,77 0F) 0.28mΩ |  |
| Constant Voltage Charge | Cycle | Initial Charging Current less than 200A Voltage 2.35~2.40V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |
|  | Standby | No limit on Initial Charging Current Voltage 2.23V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |