| PHYSICAL SPECIFICATION |
| --- |
| Nominal Voltage Nominal Capacity (10HR) | 6V 125Ah |  |
| Dimension | Length Width Container Height Total Height | 260±2mm （10.24 inches） 180±2mm (7.09 inches) 247±2mm (9.72 inches) 254±2mm (10.00 inches) |  |
| Weight | Approx. 18.8Kg (41.44lbs) |  |
| Standard Terminal | Bolt-and-nuts terminal) Bolt Type: M8 |  |
| ELECTRICAL SPECIFICATION |
| Characteristics | Discharge curves @ 25℃ (77 °F) |
| Capacity | 20 hour rate (6.25A) 10 hour rate (12.5A) 5 hour rate (21.25A) 3 hour rate (31.25A) 1hour rate (75A) | 132Ah 125Ah 107Ah 93.8Ah 75Ah |  |
| Capacity affected by temperature | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） | 102% 100% 85% |  |
| Designed life | 10 years (floating) or >750 Cycles @ 50% D.O.D |  |
| Self Discharge | 3% of capacity declined per month at (25℃) |  |
| Internal Resistance | Full charged battery (25℃,77 0F) 3mΩ |  |
| Constant Voltage Charge | Cycle | Initial Charging Current less than 31.25A Voltage 7.05~7.20V at 25℃ (77 0F ) Temperature Coefficient –15mV/℃ |  |
|  | Standby | No limit on Initial Charging Current Voltage 6.75~6.90V at 25℃ (77 0F ) Temperature Coefficient –10mV/℃ |  |