| PHYSICAL SPECIFICATION |
| --- |
| Nominal Voltage Nominal Capacity (10HR) | 12V 6.5Ah |  |
| Dimension | Length Width Container Height Total Height | 138±1mm （5.43 inches） 66±1mm (2.6 inches) 101±1mm (3.98 inches) 101±1mm (3.98 inches) |  |
| Weight | Approx. 2.0Kg (4.4lbs) |  |
| Standard Terminal | F1-Fasten Tab M01 |  |
| ELECTRICAL SPECIFICATION |
| Characteristics | Discharge curves @ 25℃ (77 °F) |
| Capacity | 10 hour rate (0.65A) 5 hour rate (1.105A) 3 hour rate (1.625A) 1hour rate (3.9A) | 6.5Ah 5.5Ah 4.9Ah 3.9Ah |  |
| Capacity affected by temperature | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） | 102% 100% 85% |  |
| Internal Resistance | Full charged battery (25℃,77 0F) 12mΩ |  |
| Discharge at 52A for 5 seconds (-10℃) | ≥9.3V |  |
| Discharge at 52A for 90seconds (-10℃) | ≥6V |  |
| Constant Voltage Charge | Cycle | Initial Charging Current less than 2.1A Voltage 14.4~15.0V at 25℃ (77 0F ) Temperature Coefficient –5mV/℃ |  |
|  | Standby | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –3.3mV/℃ |  |