| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (20HR) |  |  |  | 6V 12Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 108±1mm （4.25 inches） 71±1mm (2.80 inches) 139±1mm (5.47 inches) 139±1mm (5.47 inches) |  |  |
| Weight |  |  |  | Approx. 2.34Kg ( 5.16lbs) |  |  |
| Standard Terminal |  |  |  | Connector |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (0.6A) 10 hour rate (1.08A) 5 hour rate (2.04A) 3 hour rate (3A) 1hour rate (7.2A) |  | 12Ah 11.4Ah 10.2Ah 9Ah 7.2Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 10mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 3.6A Voltage 7.20~7.50V at 25℃ (77 0F ) Temperature Coefficient –15mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 6.75~6.90V at 25℃ (77 0F ) Temperature Coefficient –10mV/℃ |  |  |  |