| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (10HR) |  |  |  | 12V 24Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 176±1mm （6.93 inches) 166±1mm (6.54 inches) 128±1mm (5.04 inches) 128±1mm (5.04 inches) |  |  |
| Weight |  |  |  | Approx. 8.1 Kg ( 17.85lbs) |  |  |
| Standard Terminal |  |  |  | Bolt-and-nut terminal Bolt Type: M5 |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 10 hour rate (2.4A) 5 hour rate (4.08A) 3 hour rate (5.8A) 1hour rate (14.4A) |  | 24Ah 21Ah 18Ah 15Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 10mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 7.2A Voltage 14.1~14.4V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |