| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (20HR) |  |  |  | 8V 3.2Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 68±1mm (2.68 inches) 48±1mm (1.89 inches) 90±1mm (3.54 inches) 90±1mm (3.54 inches) |  |  |
| Weight |  |  |  | Approx. 0.79 Kg ( 1.74lbs) |  |  |
| Standard Terminal |  |  |  | Fasten Tab No.187E |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (0.16A) 10 hour rate (0.288A) 5 hour rate (0.544A) 3 hour rate (0.8A) 1hour rate (1.92A) |  | 3.2Ah 3.0Ah 2.8Ah 2.4Ah 2Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 25mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 0.96A Voltage 9.6~10V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 9~9.2V at 25℃ (77 0F ) Temperature Coefficient –18mV/℃ |  |  |  |