| PHYSICAL SPECIFICATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Nominal Voltage Nominal Capacity (20HR) |  |  |  | 12V 7Ah |  |  |
| Dimension |  | Length Width Container Height Total Height |  | 151±1mm （5.94 inches) 65±1mm (2.56 inches) 95±1mm (3.74 inches) 108±1mm (4.25 inches) |  |  |
| Weight |  |  |  | Approx. 2.45 Kg (5.40lbs) |  |  |
| Standard Terminal |  |  |  | Bolt-and-nut terminal Bolt Type: M5 |  |  |
| # ELECTRICAL SPECIFICATION |  |  |  |  |  |  |
| # Characteristics |  |  |  |  |  | # Discharge curves @ 25℃ (77 °F) |
| Capacity |  |  | 20 hour rate (0.35A) 10 hour rate (0.63A) 5 hour rate (1.19A) 3 hour rate (1.75A) 1hour rate (4.2A) |  | 7Ah 6.6Ah 6Ah 5.3Ah 4.2Ah |  |
| Capacity affected by temperature |  |  | 40℃ （104 0F） 25℃ （77 0F） 0℃ （32 0F） |  | 102% 100% 85% |  |
| Internal Resistance |  |  | Full charged battery (25℃,77 0F) 25mΩ |  |  |  |
| Constant Voltage Charge | Cycle |  | Initial Charging Current less than 2.1A Voltage 14.4~15.0V at 25℃ (77 0F ) Temperature Coefficient –30mV/℃ |  |  |  |
|  | Standby |  | No limit on Initial Charging Current Voltage 13.5~13.8V at 25℃ (77 0F ) Temperature Coefficient –20mV/℃ |  |  |  |